## Khost Switch Room assesment
Data Center Assessment Report
1. General Information
Data center name & location | KST-207(MOC)
Purpose (Edge, Core, DR, etc.) | Data center
Tier level (if any): Tier I / II / III
Total white space (sqm) and rack capacity | 70.35 Sqm 15 Racks Capacity
Data Center floor No & Size (cm) [L × W × H] | Second Floor(10.50 * 6.70 *3.10)
Door type (Single / double) & Dimensions [W × H] | Single(0.90 *2.60)
Assessment date & scope | 2025-12-22
2. Executive Summary
Purpose of Assessment:
Scope:
Overall Readiness Score: 65%
Key Risks: Power cable and with all the new sensors and alarms are rquired
Recommendations (Short-term / Mid-term / Long-term):
3. Facility & Infrastructure
Building & Layout | No
Map and design | No
Structural condition | good
Raised floor / slab design | Normal
Thermal Insulation (PE foam) | Yes
Hot aisle / cold aisle implementation | NO
Cable management (power & data) | Not Good
Aluminum Color Coated White Fireproof T Grid Ceiling | No
Painting | No
Physical Security | Yes
Perimeter security | Yes(door)
Access control (biometric, card, logs) | No
CCTV coverage & retention | No
Visitor management | No
4. Power Infrastructure
Utility power availability (single/dual feed) | Yes(dual feed)
UPS type, capacity & redundancy (N, N+1, 2N) | 2* 10KVA UPS N+1 redundancy
Battery health & maintenance | 10%
Generator capacity & runtime | 2*65 KVA
ATS/STS availability | Yes
Rack Power distribution Unite (AC & DC) | No
Lighting system | No
Earthing & grounding system | Yes
5. Cooling & Environmental Control
Cooling type (CRAC/AC) | AC*2
Cooling redundancy | No
Hot spots identification | No
Airflow management | No
Environmental monitoring System (temp, humidity, Water leak & Smoke) EMS | No
6. Fire Detection & Suppression
Fire detection system (VESDA / smoke detectors) | No
Fire suppression system (FM200) | No
Fire extinguisher manual Type | No
7. Standard & Compliance
International Standards (TIA-942):
8. Risks & Gaps Identified
Area | Gap / Risk | Impact | Priority
Power and Cabling under the ground poorly managed. | Power | Yes | Yes
9. Recommendations & Roadmap
Recommendation | Timeline | Estimated Cost | Priority
Short-term | 0–3 months
Mid-term | 3–12 months |  | Yes
Long-term | 1–3 years
10. Sign-off
Assessor Name & Signature: ___________________
Date: ___________________